## TOWER_LIST
Contractor: | [5 empty] | Customer: | [31 empty] | LOT 1: CONSTRUCTION OF 500KV JVARI - TSKALTUBO OVERHEAD LINE | [24 empty] | Consultant:
STRUCTURE LIST
| INSULATOR/ HARDWARE SETS FOR CONDUCTOR | [36 empty] | HARDWARE SETS FOR OPGW & EARTHWIRE | [7 empty] | NOTES
| SS : | SINGLE SUSPENSION SET | [7 empty] | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | 95-S : | SUSPENSION SET FOR 95 mm2 EW/OPGW | [6 empty] | 1- | Basic Earthing System were proposed for all Towers. The Final Earthing will determined after Soil Resistivity Tests
| DS : | DOUBLE SUSPENSION SET | [7 empty] | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | 95-T : | ANCHOR / TENSION SET FOR 95 mm2 EW/OPGW | [6 empty] | 2- | Foundation Types will be finalized after performing the Soil Investigation Test
| ST : | SINGLE TENSION SET | [7 empty] | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | 95-TSJ | SUSPENSION SET FOR 185 mm2 EW/OPGW | [6 empty] | 3- | The Distribution of Dampers are determined as per Damping Study for Conductor and EW
| 2T : | DOUBLE TENSION SET | [7 empty] | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | 185-S : | SUSPENSION SET FOR 185 mm2 EW/OPGW | [6 empty] | 4- | C.W : Counter Weight
| 3T : | TRIPLE TENSION SET | [7 empty] | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | 185-T : | ANCHOR / TENSION SET FOR 185 mm2 EW/OPGW | [6 empty] | 5- | W.S : Warning Spheres (60 cm Diameter, Red)
| JS : | JUMPER SUSPENSION SET | [7 empty] | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JB : | JOINT BOX FOR OPGW
[18 empty] | FOUNDATION | [9 empty] | ERECTION |  |  |  | STRINGING
Sl.No. | Towers | [12 empty] | Access Road |  | Soil Investigation |  | Excavation |  | Lean Concrete |  | Stub Settings |  | Concrete |  | Backfilling |  | Ground Erection |  | Crane Erection |  | Conductor |  | EW |  | OPGW |  |  |  | ANGLE POINT NO. | Line Angle Degrees | Spans | [6 empty] | CONDUCTOR | [6 empty] | OPGW |  |  |  | EARTHWIRE |  |  |  |  | Warning Spheres | GROUNDING |  |  |  | Towers
| Construction No. | Tower Type | Jvari Tskaltubo |  |  |  | X COORDINATE (m) | Y COORDINATE (m) | Z COORDINATE (m) | TODAY's PROGRESS | TOMORROW'S PLAN | STATUS | SITE ACCESS | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Date of Completion | Status | Cumulative Length (m) | FOUNDATION TYPE |  |  | Actual span (m) | Wind span (m) | Weight span (m) (at Max Temperature) | Weight to Wind Span Ratio | Line Section | RULLING SPAN ( m) | SECTION LENGTH ( m) | Conductor | Insulator Strings | Jumper String | Rigid Spacer per Jumper | Spacer damper per phase | Stock bridge damper per span per conductor (UT3) |  | OPGW Sets | Stock bridge damper per span per OPGW (UT2) |  | OPGW Joint Boxes | Earthwire Sets | Stock bridge damper per span per EW |  | NOS of UT1 TYPE STOCKBRIDGE DAMPER | NOS of UT2 TYPE STOCKBRIDGE DAMPER |  | Type | Initial Resistance (ohm) | Final Resistance (ohm) | Crossing | Remarks | Construction No.
|  |  | 1 | 2 | 3 | 4 | [47 empty] | Back Span | Ahead Span |  | Back Span | Ahead Span |  |  | Back Span | Ahead Span
1 | G1 | GANTRY | N.A | N.A | N.A | N.A | 301752.28 | 4683922.9 | 138.888 | [28 empty] | 0 |  | AP0 / SS |  |  | 43 | 53 | 1.23 |  |  |  |  | 2T |  |  |  |  | 1 | 95-TSJ |  | 1 | JB | 95-TSJ |  | 1 | 1 | 0 | [6 empty] | G1
[42 empty] | 85 |  |  |  | 1 | 85 | 85 | 400/51 |  |  |  | 3
2 | 1 | B90-3 |  |  |  |  | 301669.3 | 4683941.34 | 137.882 | Excavation |  | Active |  | 2024-01-15 | Completed | 2025-12-12 | Completed | 2026-04-05 | Today Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 85 | 5.1 | AP1 | -13.0027 |  | 183 | 224 | 1.22 |  |  |  |  | 2T-2T | 4 | 2 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 1
[42 empty] | 280.29 |  |  |  | 2 | 280.29 | 280.29 | 400/51 |  |  |  | 6 | [15 empty] | TRACK
3 | 2 | B30-3 |  |  |  |  | 301389.022 | 4683939.022 | 134.2 |  |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-04 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 365.29 | 3 | AP2 | -23.6247 |  | 280 | 250 | 0.89 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 2
[42 empty] | 279.71 |  |  |  | 3 | 291.5004 | 581.72 | 400/51 |  |  |  | 5
4 | 3 | BNS+6 |  |  |  |  | 301133.692 | 4683824.815 | 129.362 |  |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 645 | 3 |  |  |  | 291 | 353 | 1.21 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 3
[42 empty] | 302.01 | [6 empty] | 400/51 |  |  |  | 6 | [15 empty] | TRACK
5 | 4 | B60-3 |  |  |  |  | 300858 | 4683701.5 | 126.326 |  |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 947.01 | 4.1 | AP3 | 50.5638 |  | 302 | 234 | 0.77 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 4
[42 empty] | 302.56 |  |  |  | 4 | 322.4451 | 641.76 | 400/51 |  |  |  | 6 | [15 empty] | ROAD
6 | 5 | BNS+3 |  |  |  |  | 300587.151 | 4683836.335 | 127.391 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 1249.57 | 4.1 |  |  |  | 321 | 361 | 1.12 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 5
[42 empty] | 339.2 | [6 empty] | 400/51 |  |  |  | 7
7 | 6 | B60+3 |  |  |  |  | 300283.5 | 4683987.5 | 123.786 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 1588.77 | 5.1 | AP4 | -51.9286 |  | 274 | 249 | 0.91 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 6
[42 empty] | 209.33 |  |  |  | 5 | 209.33 | 209.33 | 400/51 |  |  |  | 4 | [15 empty] | ROAD, RAILWAY, MV OHDL
8 | 7 | B90+9 |  |  |  |  | 300094.5 | 4683897.5 | 120.878 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-04 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 1798.1 | 3 | AP5 | 67.6282 |  | 308 | 343 | 1.11 |  |  |  |  | 2T-2T | 2 | 2 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 7
[42 empty] | 407.44 |  |  |  | 6 | 407.44 | 407.44 | 400/51 |  |  |  | 8 | [15 empty] | ROAD, MV OHDL
9 | 8 | B30+3 |  |  |  |  | 299792.5 | 4684171 | 119.573 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2205.54 | 5.1 | AP6 | -17.7222 |  | 398 | 378 | 0.95 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 8
[42 empty] | 389.46 |  |  |  | 7 | 375.5975 | 749.46 | 400/51 |  |  |  | 8
10 | 9 | BNS+6 |  |  |  |  | 299437.945 | 4684332.152 | 117.014 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet | 15/12/2025 | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2595 | 3 |  |  |  | 375 | 414 | 1.1 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 9
[42 empty] | 360 | [6 empty] | 400/51 |  |  |  | 7
11 | 10 | B30-3 |  |  |  |  | 299110.21 | 4684481.114 | 115.154 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 30/03/2026 | Not Yet | 30/03/2026 | Not Yet | 30/03/2026 | Not Yet | 30/03/2026 | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2955 | 3 |  |  |  | 358 | 317 | 0.89 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 10
[42 empty] | 355 |  |  |  | 8 | 355 | 355 | 400/51 |  |  |  | 7
12 | 11 | B30+0 |  |  |  |  | 298787.027 | 4684628.007 | 114.498 |  |  |  | NO PERMISSION / LAND OWNER | 2024-12-12 | Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3310 | 4.1 |  |  |  | 345 | 350 | 1.01 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 11
[42 empty] | 335 |  |  |  | 9 | 337.5278 | 675 | 400/51 |  |  |  | 7 | [15 empty] | ROAD, MV OHDL
13 | 12 | BNS+3 |  |  |  |  | 298482.051 | 4684766.624 | 112.108 | Excavation |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-05 | Today Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3645 | 4.1 |  |  |  | 338 | 374 | 1.11 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 12
[42 empty] | 340 | [6 empty] | 400/51 |  |  |  | 7
14 | 13 | B30-3 |  |  |  |  | 298172.523 | 4684907.31 | 108.707 | Lean Concrete |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-04 | Completed | 2026-04-05 | Today Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3985 | 5.1 |  |  |  | 345 | 286 | 0.83 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 13
[42 empty] | 350 |  |  |  | 10 | 344.3408 | 1032.79 | 400/51 |  |  |  | 7
15 | 14 | BNS+6 |  |  |  |  | 297853.892 | 4685052.135 | 108.648 | Excavation |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-05 | Today Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 4335 | 3 |  |  |  | 345 | 383 | 1.11 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 14
[42 empty] | 340 | [6 empty] | 400/51 |  |  |  | 7
16 | 15 | BNS+6 |  |  |  |  | 297544.364 | 4685192.821 | 106.444 | Lean Concrete |  | Active |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2026-04-04 | Completed | 2026-04-05 | Today Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 4675 | 5.1 |  |  |  | 342 | 376 | 1.1 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 15
[42 empty] | 342.79 | [6 empty] | 400/51 |  |  |  | 7
17 | 16 | B60-3 |  |  |  |  | 297232.3 | 4685334.66 | 103.194 | Access Road |  |  |  | 2026-04-05 | Today Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 5017.79 | 3 | AP7 | 54.309 |  | 365 | 296 | 0.81 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 16
[42 empty] | 387.21 |  |  |  | 11 | 367.7791 | 1091.3 | 400/51 |  |  |  | 8
18 | 17 | BNS+9 |  |  |  |  | 297156.77 | 4685714.436 | 101.729 | Access Road |  |  |  | 2026-04-05 | Today Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 5405 | 3 |  |  |  | 386 | 439 | 1.14 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  | CW: 100 kg | 17
[42 empty] | 385 | [6 empty] | 400/51 |  |  |  | 7 | [15 empty] | STREAM
19 | 18 | BNS+9 |  |  |  |  | 297081.671 | 4686092.04 | 102.407 | Access Road |  |  |  | 2026-04-05 | Today Completed | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 5790 | 4.1 |  |  |  | 352 | 396 | 1.13 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 18
[42 empty] | 319.09 | [6 empty] | 400/51 |  |  |  | 6 | [15 empty] | ROAD
20 | 19 | B30-3 |  |  |  |  | 297019.43 | 4686405 | 103.047 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 6109.09 | 4.1 | AP8 | -17.6138 |  | 325 | 262 | 0.81 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 19
[42 empty] | 330.91 |  |  |  | 12 | 349.2338 | 695.96 | 400/51 |  |  |  | 7
21 | 20 | BNS+3 |  |  |  |  | 296859.698 | 4686694.807 | 104.096 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 6440 | 5.1 |  |  |  | 348 | 385 | 1.11 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 20
[42 empty] | 365.05 | [6 empty] | 400/51 |  |  |  | 7 | [15 empty] | MV OHDL
22 | 21 | B30-3 |  |  |  |  | 296683.489 | 4687014.508 | 106.855 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 6805.05 | 3 | AP9 | 13.4196 |  | 388 | 331 | 0.85 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 21
[42 empty] | 409.95 |  |  |  | 13 | 420.3338 | 839.95 | 400/51 |  |  |  | 8
23 | 22 | BNS+12 |  |  |  |  | 296574.33 | 4687409.662 | 108.497 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 7215 | 5.1 |  |  |  | 420 | 474 | 1.13 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 22
[42 empty] | 430 | [6 empty] | 400/51 |  |  |  | 8
24 | 23 | B30-3 |  |  |  |  | 296459.833 | 4687824.138 | 122.386 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 7645 | 3 |  |  |  | 428 | 362 | 0.85 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 23
[42 empty] | 425 |  |  |  | 14 | 402.3763 | 1197.29 | 400/51 |  |  |  | 8
25 | 24 | BNS+6 |  |  |  |  | 296346.668 | 4688233.795 | 136.676 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 8070 | 3 |  |  |  | 420 | 476 | 1.13 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 24
[42 empty] | 415 | [6 empty] | 400/51 |  |  |  | 8 | [15 empty] | TRACK
26 | 25 | BNS+3 |  |  |  |  | 296236.165 | 4688633.813 | 143.401 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 8485 | 4.1 |  |  |  | 386 | 456 | 1.18 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 25
[42 empty] | 357.29 | [6 empty] | 400/51 |  |  |  | 7
27 | 26 | B30+3 |  |  |  |  | 296141.03 | 4688978.2 | 125.932 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 8842.29 | 4.1 | AP10 | -13.6257 |  | 360 | 247 | 0.69 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 26
[42 empty] | 362.71 |  |  |  | 16 | 353.598 | 1407.34 | 400/51 |  |  |  | 7
28 | 27 | BNS+3 |  |  |  |  | 295964.805 | 4689295.227 | 144.908 |  |  |  |  | 2024-12-12 | Completed | 2025-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 2024-12-12 | Completed | 9205 | 5.1 |  |  |  | 349 | 376 | 1.08 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 27
[42 empty] | 335 | [6 empty] | 400/51 |  |  |  | 7
29 | 28 | BNS+6 |  |  |  |  | 295802.045 | 4689588.031 | 152.002 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 9540 | 3 |  |  |  | 333 | 382 | 1.15 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 28
[42 empty] | 330 | [6 empty] | 400/51 |  |  |  | 7
30 | 29 | BNS-3 |  |  |  |  | 295641.715 | 4689876.465 | 156.385 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 9870 | 5.1 |  |  |  | 356 | 450 | 1.26 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 29
[42 empty] | 379.63 | [6 empty] | 400/51 |  |  |  | 7
31 | 30 | B60-3 |  |  |  |  | 295457.27 | 4690208.28 | 119.053 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 10249.63 | 3 | AP11 | -42.8413 |  | 376 | 223 | 0.59 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 30
[42 empty] | 370.37 |  |  |  | 16 | 336.8269 | 1001.04 | 400/51 |  |  |  | 7 | [15 empty] | TRACK, STREAM, MV OHDL
32 | 31 | BNS+9 |  |  |  |  | 295105.211 | 4690323.286 | 122.855 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 10620 | 3 |  |  |  | 340 | 382 | 1.12 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 31
[42 empty] | 310 | [6 empty] | 400/51 |  |  |  | 6 | [15 empty] | ROAD
33 | 32 | BNS+6 |  |  |  |  | 294810.535 | 4690419.547 | 127.766 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 10930 | 4.1 |  |  |  | 315 | 346 | 1.1 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 32
[42 empty] | 320.67 | [6 empty] | 400/51 |  |  |  | 6
34 | 33 | B30-3 |  |  |  |  | 294505.72 | 4690519.12 | 130.617 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 11250.67 | 4.1 | AP12 | 27.8332 |  | 378 | 274 | 0.72 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 33
[42 empty] | 434.33 |  |  |  | 17 | 435.7569 | 871.5 | 400/51 |  |  |  | 8
35 | 34 | BNS+12 |  |  |  |  | 294203.591 | 4690831.151 | 148.031 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 11685 | 5.1 |  |  |  | 437 | 493 | 1.13 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  | CW: 200 kg | 34
[42 empty] | 437.17 | [6 empty] | 400/51 |  |  |  | 9 | [15 empty] | ROAD, MV OHDL
36 | 35 | B30-3 |  |  |  |  | 293899.49 | 4691145.22 | 192.269 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 12122.17 | 3 | AP13 | 3.7687 |  | 458 | 601 | 1.31 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 35
[42 empty] | 477.83 |  |  |  | 18 | 477.83 | 477.83 | 400/51 |  |  |  | 9
37 | 36 | B30+0 |  |  |  |  | 293590.386 | 4691509.606 | 161.858 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 12600 | 5.1 |  |  |  | 460 | 299 | 0.65 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 36
[42 empty] | 440 |  |  |  | 19 | 394.0545 | 1530 | 400/51 |  |  |  | 9
38 | 37 | BNS+3 |  |  |  |  | 293305.754 | 4691845.143 | 197.254 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13040 | 3 |  |  |  | 433 | 495 | 1.14 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 37
[42 empty] | 425 | [6 empty] | 400/51 |  |  |  | 8
39 | 38 | BNS+6 |  |  |  |  | 293030.826 | 4692169.241 | 209.151 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13465 | 3 |  |  |  | 363 | 418 | 1.15 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 38
[42 empty] | 300 | [6 empty] | 400/51 |  |  |  | 6 | [15 empty] | ROAD, MV OHDL
40 | 39 | BNS+3 |  |  |  |  | 292836.759 | 4692398.016 | 208.052 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13765 | 4.1 |  |  |  | 333 | 375 | 1.13 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 39
[42 empty] | 365 | [6 empty] | 400/51 |  |  |  | 7 | [15 empty] | TRACK
41 | 40 | B30-3 |  |  |  |  | 292600.644 | 4692676.359 | 195.984 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14130 | 4.1 |  |  |  | 323 | 216 | 0.67 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 40
[42 empty] | 280 |  |  |  | 20 | 363.8602 | 1050.42 | 400/51 |  |  |  | 5
42 | 41 | BNS+3 |  |  |  |  | 292419.515 | 4692889.882 | 202.976 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14410 | 5.1 |  |  |  | 350 | 406 | 1.16 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 41
[42 empty] | 420 | [6 empty] | 400/51 |  |  |  | 8 | [15 empty] | TRACK
43 | 42 | BNS-3 |  |  |  |  | 292147.822 | 4693210.167 | 208.471 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14830 | 3 |  |  |  | 386 | 489 | 1.27 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 42
[42 empty] | 350.42 | [6 empty] | 400/51 |  |  |  | 7 | [15 empty] | MV OHDL
44 | 43 | B30+0 |  |  |  |  | 291921.14 | 4693477.39 | 173.227 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 15180.42 | 5.1 | AP14 | 24.8755 |  | 339 | 159 | 0.47 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 43
[42 empty] | 324.58 |  |  |  | 21 | 355.5443 | 704.58 | 400/51 |  |  |  | 6 | [15 empty] | TRACK
45 | 44 | BNS-3 |  |  |  |  | 291834.77 | 4693790.27 | 198.96 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 15505 | 3 |  |  |  | 353 | 457 | 1.29 |  |  |  |  | DS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 44
[42 empty] | 380 | [6 empty] | 400/51 |  |  |  | 7 | [15 empty] | MV OHDL
46 | 45 | B30-3 |  |  |  |  | 291733.654 | 4694156.57 | 191.034 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 15885 | 3 |  |  |  | 329 | 167 | 0.51 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 45
[42 empty] | 275 |  |  |  | 22 | 270.1389 | 540 | 400/51 |  |  |  | 5 | [15 empty] | TRACK
47 | 46 | BNS+3 |  |  |  |  | 291660.478 | 4694421.655 | 222.396 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16160 | 4.1 |  |  |  | 272 | 339 | 1.25 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 46
[42 empty] | 265 | [6 empty] | 400/51 |  |  |  | 5
48 | 47 | BLC+12 |  |  |  |  | 291589.963 | 4694677.101 | 232.72 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16425 | 4.1 |  |  |  | 305 | 569 | 1.87 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 47
[42 empty] | 338.09 |  |  |  | 23 | 338.09 | 338.09 | 400/51 |  |  |  | 7
49 | 48 | B90C |  |  |  |  | 291500 | 4695003 | 196.258 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16763.09 | 5.1 | AP15 | 16.0565 |  | 263 | 69 | 0.26 |  |  |  |  | 2T-2T | 2 | 2 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 48
[42 empty] | 183.51 |  |  |  | 24 | 183.51 | 183.51 | 400/51 |  |  |  | 4 | [15 empty] | UNDER CROSSING 500 KV OHTL
50 | 49 | B90C |  |  |  |  | 291502 | 4695186.5 | 197.635 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16946.6 | 3 | AP16 | -43.8679 |  | 236 | 43 | 0.18 |  |  |  |  | 2T-2T | 4 | 2 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 49
[42 empty] | 283.4 |  |  |  | 25 | 297.5929 | 593.4 | 400/51 |  |  |  | 6
51 | 50 | BNS-3 |  |  |  |  | 291307.842 | 4695392.943 | 244.69 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 17230 | 5.1 |  |  |  | 300 | 461 | 1.54 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 50
[42 empty] | 310 | [6 empty] | 400/51 |  |  |  | 6
52 | 51 | B30-3 |  |  |  |  | 291095.461 | 4695618.763 | 257.461 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 17540 | 3 |  |  |  | 392 | 297 | 0.76 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 51
[42 empty] | 470 |  |  |  | 26 | 378.5951 | 1022.32 | 400/51 |  |  |  | 9
53 | 52 | BNS+12 |  |  |  |  | 290773.464 | 4695961.134 | 301.713 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 18010 | 3 |  |  |  | 385 | 443 | 1.15 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  | CW: 100 kg | 52
[42 empty] | 295 | [6 empty] | 400/51 |  |  |  | 6
54 | 53 | BNS+6 |  |  |  |  | 290571.359 | 4696176.026 | 336.18 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 18305 | 4.1 |  |  |  | 278 | 529 | 1.9 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 53
[42 empty] | 257.32 | [6 empty] | 400/51 |  |  |  | 5
55 | 54 | B60+6 |  |  |  |  | 290395.07 | 4696363.47 | 301.585 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 18562.32 | 4.1 | AP17 | 42.2058 |  | 340 | 57 | 0.17 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 54
[42 empty] | 417.68 |  |  |  | 27 | 417.68 | 417.68 | 400/51 |  |  |  | 8
56 | 55 | B30+12 |  |  |  |  | 290387.506 | 4696781.082 | 347.738 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 18980 | 5.1 |  |  |  | 343 | 367 | 1.07 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 55
[42 empty] | 263 |  |  |  | 28 | 270.2721 | 540 | 400/51 |  |  |  | 5
57 | 56 | BNS-3 |  |  |  |  | 290382.743 | 4697044.039 | 393.693 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 19243 | 3 |  |  |  | 272 | 535 | 1.97 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 56
[42 empty] | 277 | [6 empty] | 400/51 |  |  |  | 5
58 | 57 | B30+12 |  |  |  |  | 290377.727 | 4697320.994 | 337.678 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 19520 | 5.1 |  |  |  | 353 | 597 | 1.69 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 57
[42 empty] | 399.07 |  |  |  | 29 | 399.07 | 399.07 | 400/51 |  |  |  | 8 | [15 empty] | MV OHDL
59 | 58 | B30+3 |  |  |  |  | 290370.5 | 4697720 | 195.062 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 19919.07 | 3 | AP18 | -29.4281 |  | 401 | 37 | 0.09 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 58
[42 empty] | 375.93 |  |  |  | 30 | 375.93 | 375.93 | 400/51 |  |  |  | 7 | [15 empty] | ROAD, TRACK
60 | 59 | B30-3 |  |  |  |  | 290179.895 | 4698044.025 | 194.275 | [5 empty] | Not Yet | 2025-12-12 | Completed |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 20295 | 3 |  |  |  | 354 | 253 | 0.71 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 59
[42 empty] | 330 |  |  |  | 31 | 330 | 330 | 400/51 |  |  |  | 7 | [11 empty] | 8 WS |  |  |  | STREAM, TRACK
61 | 60 | B30+0 |  |  |  |  | 290012.578 | 4698328.462 | 218.512 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 20625 | 4.1 |  |  |  | 303 | 182 | 0.6 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 60
[42 empty] | 270 |  |  |  | 32 | 303.7889 | 598.94 | 400/51 |  |  |  | 5
62 | 61 | BNS+3 |  |  |  |  | 289875.681 | 4698561.184 | 268.483 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 20895 | 4.1 |  |  |  | 304 | 356 | 1.17 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 61
[42 empty] | 328.94 | [6 empty] | 400/51 |  |  |  | 7
63 | 62 | B30+12 |  |  |  |  | 289708.9 | 4698844.71 | 308.761 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 21223.94 | 5.1 | AP19 | 16.0256 |  | 321 | 223 | 0.69 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 62
[42 empty] | 301.06 |  |  |  | 33 | 301.06 | 301.06 | 400/51 |  |  |  | 6
64 | 63 | BLC-6 |  |  |  |  | 289633.825 | 4699136.257 | 402.424 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 21525 | 3 |  |  |  | 386 | 844 | 2.19 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 63
[42 empty] | 455 |  |  |  | 34 | 455 | 455 | 400/51 |  |  |  | 9
65 | 65 | B30+12 |  |  |  |  | 289520.363 | 4699576.883 | 304.065 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 21980 | 5.1 |  |  |  | 410 | 101 | 0.25 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 65
[42 empty] | 358.053 |  |  |  | 2 | 506.04 | 506.04 | 400/51 |  |  |  | 7
2 | 66 | B30-3 | +0 LE | -1.5 LE | +1.5 LE | +3 LE | 289441.01 | 4699926.03 | 354.116 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 358.053 | 3 | P2-AP02 | -10.7241 |  | 434 | 667 | 1.5369 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 66
[42 empty] | 506.04 |  |  |  | 3 | 494.19 | 494.19 | 400/51
3 | 67 | B30+0 | +1.5 LE | +0 LE | +0 LE | +0 LE | 289239 | 4700390 | 298.742 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 864.093 | 3 | P2-AP03 | -5.5266 |  | 503 | 267 | 0.53082 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 67
[42 empty] | 494.19 |  |  |  | 4 | 654.765 | 654.765 | 400/51
4 | 68 | BLS+12 | +0 LE | +3 LE | +0 LE | -1.5 LE | 288999 | 4700822 | 336.829 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 1358.283 | 4.1 | P2-AP04 | -6.5289 |  | 580 | 525 | 0.90517 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 185-T | 1 | 2 |  | 185-T | 1 | 2 | 1 | 2 |  | Step-1 |  |  |  |  | 68
[42 empty] | 654.765 |  |  |  | 5 | 162.304 | 162.304 | 400/51
5 | 70 | BLS+12 | -3 LE | +3 LE | +4.5 LE | -3 LE | 288618 | 4701354.5 | 437.305 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2013.048 | 4.1 | P2-AP06 | -30.6154 |  | 413 | 719 | 1.7409 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 185-T | 2 | 1 |  | 185-T | 2 | 1 | 1 | 2 |  | Step-1 |  |  |  |  | 70
[42 empty] | 162.304 |  |  |  | 6 | 483.255 | 483.255 | 400/51
6 | 71 | B90+12 | -3 LE | +1.5 LE | +1.5 LE | -3 LE | 288469.5 | 4701420 | 413.475 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2175.352 | 5.1 | P2-AP07 | 40.3761 |  | 324 | 158 | 0.48765 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 71
[42 empty] | 483.255 |  |  |  | 7 | 341.721 | 341.721 | 400/51
7 | 72 | B30+0 | +1.5 LE | +0 LE | +0 LE | +1.5 LE | 288259 | 4701855 | 444.185 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 2658.607 | 3 | P2-AP08 | -8.5649 |  | 413 | 450 | 1.0896 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 72
[42 empty] | 341.721 |  |  |  | 8 | 395 | 758.286 | 400/51
8 | 73 | B30-3 | +0 LE | +1.5 LE | +0 LE | +1.5 LE | 288066 | 4702137 | 451.138 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3000.328 | 5.1 | P2-AP09 | 4.6615 |  | 393 | 346 | 0.88041 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 73
[42 empty] | 444.175 | [6 empty] | 400/51
9 | 74 | BNS+12 | +0 LE | +0 LE | +0 LE | +0 LE | 287845.753 | 4702522.724 | 460.067 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3444.503 | 3 |  |  |  | 380 | 388 | 1.0211 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 74
[42 empty] | 314.111 |  |  |  | 9 | 463.684 | 463.684 | 400/51
10 | 75 | B30+12 | +0 LE | -1.5 LE | +0 LE | +0 LE | 287690 | 4702795.5 | 475.889 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 3758.614 | 3 | P2-AP10 | -13.3425 |  | 389 | 482 | 1.2391 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 75
[42 empty] | 463.684 |  |  |  | 10 | 424.081 | 424.081 | 400/51
11 | 76 | B30+6 | +0 LE | +0 LE | +0 LE | +0 LE | 287373.362 | 4703134.238 | 468.373 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 4222.298 | 4.1 | P2-AP11 | -15.434 |  | 447 | 609 | 1.3624 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 76
[42 empty] | 424.081 |  |  |  | 11 | 296.637 | 296.637 | 400/51
12 | 77 | B30-3 | +0 LE | +0 LE | +1.5 LE | +1.5 LE | 287011.763 | 4703355.803 | 404.578 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 4646.379 | 4.1 | P2-AP12 | 14.0564 |  | 363 | 156 | 0.42975 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 77
[42 empty] | 296.637 |  |  |  | 12 | 351.174 | 351.174 | 400/51
13 | 78 | B30-3 | -1.5 LE | +1.5 LE | +3 LE | +1.5 LE | 286804.046 | 4703567.574 | 408.792 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 4943.016 | 5.1 | P2-AP13 | -22.5536 |  | 324 | 398 | 1.2284 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 78
[42 empty] | 351.174 |  |  |  | 13 | 595.757 | 595.757 | 400/51
14 | 79 | B30+3 | -3 LE | +3 LE | +0 LE | -3 LE | 286480.789 | 4703704.789 | 385 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 5294.19 | 3 | P2-AP14 | -8.4672 |  | 480 | 190 | 0.39583 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 79
[42 empty] | 595.757 |  |  |  | 14 | 404.7 | 1193.798 | 400/51
15 | 80 | B30+0 | -3 LE | +1.5 LE | +3 LE | -1.5 LE | 285904.094 | 4703854.287 | 511.503 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 5889.947 | 5.1 | P2-AP15 | -0.3024 |  | 472 | 766 | 1.6229 |  |  |  |  | 2T-2T | 3 |  |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 80
[42 empty] | 334.25 | [6 empty] | 400/51
16 | 81 | BNS+6 | -1.5 LE | +1.5 LE | +3 LE | -1.5 LE | 285580.101 | 4703936.453 | 489.659 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 6224.197 | 3 |  |  |  | 387 | 399 | 1.031 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 81
[42 empty] | 439.562 | [6 empty] | 400/51
17 | 82 | BNS+12 | -1.5 LE | +1.5 LE | +1.5 LE | +0 LE | 285154.027 | 4704044.508 | 459.722 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 6663.759 | 3 |  |  |  | 431 | 462 | 1.0719 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 82
[42 empty] | 419.986 |  |  |  | 15 | 929.969 | 929.969 | 400/51
18 | 83 | BLS+0 | -1.5 LE | +0 LE | +3 LE | -1.5 LE | 284746.928 | 4704147.751 | 438.673 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 7083.745 | 4.1 |  |  |  | 679 | 829 | 1.2209 |  |  |  |  | 3T-3T | 6 |  |  | 1 | 3 | 185-T | 1 | 1 | JB | 185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 83
[42 empty] | 929.969 |  |  |  | 16 | 318.6 | 595.517 | 500/204
19 | 84 | BLS-6 | +1.5 LE | -1.5 LE | +0 LE | +3 LE | 283845.496 | 4704376.36 | 333.491 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 8013.714 | 4.1 |  |  |  | 582 | 346 | 0.5945 |  |  |  |  | 3T-3T | 6 |  |  | 3 | 1 | 185-T | 1 | 1 | JB | 185-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 84
[42 empty] | 227.286 | [6 empty] | 400/51
20 | 85 | BNS+9 | +1.5 LE | -1.5 LE | -1.5 LE | +0 LE | 283625.185 | 4704432.233 | 319.354 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 8241 | 5.1 |  |  |  | 298 | 394 | 1.3221 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 85
[42 empty] | 368.231 |  |  |  | 17 | 399.33 | 399.33 | 400/51
21 | 86 | B60+6 | +0 LE | -1.5 LE | +1.5 LE | +3 LE | 283268.253 | 4704522.753 | 293 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 8609.231 | 3 | P2-AP16 | 51.0874 |  | 384 | 323 | 0.84115 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 86
[42 empty] | 399.33 |  |  |  | 18 | 242.486 | 242.486 | 400/51
22 | 87 | B60-3 | +1.5 LE | +1.5 LE | +0 LE | +0 LE | 283101.5 | 4704885.6 | 293.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 9008.561 | 5.1 | P2-AP17 | 35.0706 |  | 321 | 229 | 0.7134 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 87
[42 empty] | 242.486 |  |  |  | 19 | 360.821 | 360.821 | 400/51
23 | 88 | B30+6 | -1.5 LE | +0 LE | +1.5 LE | +0 LE | 283145.226 | 4705124.111 | 301.019 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 9251.047 | 3 | P2-AP18 | 15.4932 |  | 302 | 334 | 1.106 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 88
[42 empty] | 360.821 |  |  |  | 20 | 525.016 | 525.016 | 400/51
24 | 89 | B60+3 | +0 LE | +0 LE | +0 LE | +0 LE | 283302.73 | 4705448.74 | 316.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 9611.868 | 3 | P2-AP19 | -37.8732 |  | 443 | 458 | 1.0339 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 89
[42 empty] | 525.016 |  |  |  | 21 | 437.471 | 437.471 | 400/51
25 | 90 | B60-3 | +0 LE | +0 LE | +0 LE | +0 LE | 283193.65 | 4705962.3 | 334.533 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 10136.884 | 4.1 | P2-AP20 | 41.2553 |  | 482 | 438 | 0.90871 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 90
[42 empty] | 437.471 |  |  |  | 22 | 454.308 | 454.308 | 400/51
26 | 91 | B30-3 | +0 LE | +0 LE | +0 LE | +0 LE | 283407.5 | 4706343.94 | 362.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 10574.355 | 4.1 | P2-AP21 | 9.4058 |  | 446 | 558 | 1.2511 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 91
[42 empty] | 454.308 |  |  |  | 23 | 406.81 | 406.81 | 400/51
27 | 92 | B30-3 | +0 LE | +1.5 LE | +0 LE | -1.5 LE | 283691.365 | 4706698.646 | 349.098 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 11028.663 | 5.1 | P2-AP22 | -25.2816 |  | 431 | 435 | 1.0093 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 92
[42 empty] | 406.81 |  |  |  | 24 | 456.93 | 456.93 | 400/51
28 | 93 | B30-3 | -1.5 LE | +1.5 LE | +3 LE | +0 LE | 283785.56 | 4707094.4 | 336.392 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 11435.473 | 3 | P2-AP23 | -1.1818 |  | 432 | 367 | 0.84954 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 93
[42 empty] | 456.93 |  |  |  | 25 | 298.422 | 298.422 | 400/51
29 | 94 | B30-3 | +0 LE | +0 LE | +0 LE | +0 LE | 283882.17 | 4707541 | 348.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 11892.403 | 5.1 | P2-AP24 | -15.1129 |  | 378 | 367 | 0.9709 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 94
[42 empty] | 298.422 |  |  |  | 26 | 345.425 | 345.425 | 400/51
30 | 95 | B30-3 | +1.5 LE | +1.5 LE | +1.5 LE | +0 LE | 283867.038 | 4707839.038 | 360.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 12190.825 | 3 | P2-AP25 | 6.749 |  | 322 | 304 | 0.9441 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 95
[42 empty] | 345.425 |  |  |  | 27 | 566.789 | 566.789 | 400/51
31 | 96 | B30-3 | +0 LE | +0 LE | +0 LE | +1.5 LE | 283890.186 | 4708183.687 | 380 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 12536.25 | 3 | P2-AP26 | 6.5654 |  | 457 | 608 | 1.3304 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 96
[42 empty] | 566.789 |  |  |  | 28 | 290.277 | 290.277 | 400/51
32 | 97 | B30-3 | -1.5 LE | +0 LE | +1.5 LE | +0 LE | 283992.58 | 4708741.15 | 339.839 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13103.039 | 4.1 | P2-AP27 | 0.7955 |  | 429 | 384 | 0.8951 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 97
[42 empty] | 290.277 |  |  |  | 29 | 513.615 | 513.615 | 400/51
33 | 98 | B60-3 | +1.5 LE | +0 LE | +0 LE | +1.5 LE | 284048.979 | 4709025.896 | 330.104 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13393.316 | 4.1 | P2-AP28 | 46.4801 |  | 404 | 231 | 0.57178 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 98
[42 empty] | 513.615 |  |  |  | 30 | 289.892 | 289.892 | 400/51
34 | 99 | B30-3 | +1.5 LE | +1.5 LE | -3 LE | -1.5 LE | 284483.039 | 4709300.472 | 391.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 13906.931 | 5.1 | P2-AP29 | -15.4584 |  | 413 | 200 | 0.48426 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 99
[42 empty] | 289.892 |  |  |  | 31 | 265.837 | 265.837 | 400/51
35 | 100 | B30+3 | +3 LE | +1.5 LE | -3 LE | +0 LE | 284677.86 | 4709515.14 | 489.391 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14196.823 | 3 | P2-AP30 | 12.5423 |  | 290 | 415 | 1.431 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 100
[42 empty] | 265.837 |  |  |  | 32 | 259.34 | 259.34 | 400/51
36 | 101 | B90-3 | +3 LE | +3 LE | -1.5 LE | -1.5 LE | 284895 | 4709668.5 | 556.749 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14462.66 | 5.1 | P2-AP31 | -77.0555 |  | 266 | 451 | 1.6955 |  |  |  |  | 2T-2T | 4 |  |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 101
[42 empty] | 259.34 |  |  |  | 33 | 489.686 | 489.686 | 400/51
37 | 102 | B30+0 | -1.5 LE | +1.5 LE | +1.5 LE | +0 LE | 284796.642 | 4709908.465 | 566.44 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 14722 | 3 |  |  |  | 379 | 647 | 1.7071 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 102
[42 empty] | 489.686 |  |  |  | 34 | 391.738 | 391.738 | 400/51
38 | 103 | B30+12 | -3 LE | +3 LE | +3 LE | -3 LE | 284610.923 | 4710361.566 | 462.79 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 15211.686 | 3 | P2-AP32 | 6.6155 |  | 445 | 220 | 0.49438 |  |  |  |  | 2T-2T | 3 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 103
[42 empty] | 391.738 |  |  |  | 35 | 581.369 | 581.369 | 400/51
39 | 104 | B30+6 | -1.5 LE | +1.5 LE | +1.5 LE | -1.5 LE | 284505.1 | 4710738.74 | 473.593 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 15603.424 | 4.1 | P2-AP33 | -12.8903 |  | 487 | 439 | 0.90144 |  |  |  |  | 2T-2T | 2 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 104
[42 empty] | 581.369 |  |  |  | 36 | 422.297 | 422.297 | 400/51
40 | 105 | B30+12 | +0 LE | +1.5 LE | +1.5 LE | +0 LE | 284227.136 | 4711249.353 | 499.5 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16184.793 | 4.1 | P2-AP34 | 21.661 |  | 502 | 592 | 1.1793 |  |  |  |  | 2T-2T | 1 |  |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 105
[42 empty] | 422.297 |  |  |  | 37 | 818.936 | 818.936 | 400/51
41 | 106 | BLS+6 | -3 LE | +3 LE | +3 LE | -1.5 LE | 284176.39 | 4711668.59 | 498.33 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 16607.09 | 5.1 | P2-AP35 | -45.0887 |  | 623 | 812 | 1.3034 |  |  |  |  | 3T-3T | 4 |  |  | 1 | 3 | 185-T | 1 | 2 | JB | 185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 106
[42 empty] | 818.936 |  |  |  | 38 | 346.212 | 346.212 | 500/204
42 | 110 | BLS+12 (Part-3) | -3 LE | +3 LE | +3 LE | -1.5 LE | 283531.144 | 4712172.886 | 418.72 |  |  |  | NO PERMISSION / NO PERMIT |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 17426.026 | 3 | P2-AP36 | 2.0107 |  | 585 | 420 | 0.71795 |  |  |  |  | 3T-3T | 6 |  |  | 3 | 1 | 185-T | 2 | 1 |  | 185-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 110
[42 empty] | 346.212 | [6 empty] | 400/51
111 | 112 | BNS+9 |  |  |  |  | 283181.222 | 4712591.44 | 435.852 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 38285 | 5.1 |  |  |  | 258 | 310 | 1.2 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 112
[42 empty] | 295 | [6 empty] | 400/51 |  |  |  | 6
112 | 113 | BNS+3 |  |  |  |  | 283064.057 | 4712862.175 | 488.201 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 38580 | 3 |  |  |  | 303 | 359 | 1.18 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 113
[42 empty] | 305 | [6 empty] | 400/51 |  |  |  | 6
113 | 114 | BNS+6 |  |  |  |  | 282942.92 | 4713142.087 | 517.956 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 38885 | 3 |  |  |  | 313 | 361 | 1.15 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 114
[42 empty] | 318.1 | [6 empty] | 400/51 |  |  |  | 6
114 | 115 | B30-3 |  |  |  |  | 282816.58 | 4713434.02 | 547.816 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 39203.1 | 4.1 | AP37 | 9.7765 |  | 309 | 227 | 0.73 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 115
[42 empty] | 296.9 |  |  |  | 68 | 282.6861 | 562.82 | 400/51 |  |  |  | 6
115 | 116 | BNS+12 |  |  |  |  | 282746.641 | 4713722.566 | 574.557 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 39500 | 4.1 |  |  |  | 283 | 365 | 1.29 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 116
[42 empty] | 265.92 | [6 empty] | 400/51 |  |  |  | 5
116 | 117 | B30-3 |  |  |  |  | 282684 | 4713981 | 607.874 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 39765.92 | 5.1 | AP38 | 5.1108 |  | 258 | 311 | 1.21 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 117
[42 empty] | 249.08 |  |  |  | 69 | 249.08 | 249.08 | 400/51 |  |  |  | 5
117 | 118 | B30-3 |  |  |  |  | 282647.122 | 4714227.338 | 612.65 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 40015 | 3 |  |  |  | 344 | 187 | 0.54 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 118
[42 empty] | 435 |  |  |  | 70 | 435 | 435 | 400/51 |  |  |  | 8 | [11 empty] | 10 W.S
118 | 119 | BLC+0 |  |  |  |  | 282582.72 | 4714657.54 | 671.152 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 40450 | 5.1 | AP39 | 0.9301 |  | 549 | 325 | 0.59 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 119
[42 empty] | 614.78 |  |  |  | 71 | 614.78 | 614.78 | 400/51 |  |  |  | 12
119 | 120 | BLC+18 |  |  |  |  | 282501.58 | 4715266.95 | 889.47 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 41064.78 | 3 | AP40 | -3.7734 |  | 437 | 561 | 1.28 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 120
[42 empty] | 200.99 |  |  |  | 72 | 200.99 | 200.99 | 400/51 |  |  |  | 4
120 | 121 | BLS-6 |  |  |  |  | 282462 | 4715464 | 991.822 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 41265.77 | 3 | AP41 | -38.9729 |  | 413 | 1024 | 2.48 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 1 | 2 |  | Step-1 |  |  |  |  | 121
[42 empty] | 593.71 |  |  |  | 73 | 593.71 | 593.71 | 400/51 |  |  |  | 11 | [11 empty] | 14 W.S
121 | 122 | B60+12 |  |  |  |  | 282005 | 4715843 | 829.856 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 41859.48 | 4.1 | AP42 | 52.0894 |  | 470 | 22 | 0.05 |  |  |  |  | 2T-2T | 1 | 3 |  | 2 | 1 | 95-T | 2 | 1 | JB | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 122
[42 empty] | 325.87 |  |  |  | 74 | 288.3408 | 547.94 | 400/51 |  |  |  | 6
122 | 123 | BNS+3 |  |  |  |  | 282015.003 | 4716168.718 | 880.081 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 42185.35 | 4.1 |  |  |  | 276 | 341 | 1.24 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 123
[42 empty] | 222.07 | [6 empty] | 400/51 |  |  |  | 4
123 | 124 | B30-3 |  |  |  |  | 282021.82 | 4716390.68 | 901.91 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 42407.42 | 5.1 | AP43 | 18.7086 |  | 337 | 166 | 0.49 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 124
[42 empty] | 442.93 |  |  |  | 75 | 442.93 | 442.93 | 400/51 |  |  |  | 9
124 | 125 | B30+3 |  |  |  |  | 282176.704 | 4716805.651 | 986.85 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 42850.35 | 3 |  |  |  | 356 | 266 | 0.75 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 125
[42 empty] | 245.24 |  |  |  | 76 | 245.24 | 245.24 | 400/51 |  |  |  | 5
125 | 126 | B60+12 |  |  |  |  | 282262.46 | 4717035.41 | 1066.345 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 43095.59 | 5.1 | AP44 | -40.7452 |  | 372 | 220 | 0.59 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 126
[42 empty] | 435.59 |  |  |  | 77 | 435.59 | 435.59 | 400/51 |  |  |  | 8
126 | 127 | BLS+0 |  |  |  |  | 282111.5 | 4717444 | 1286.496 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 43531.18 | 3 | AP45 | 4.8613 |  | 655 | 1506 | 2.3 |  |  |  |  | 2T-3T | 3 | 3 |  | 1 | 2 | 95-T/185-T | 1 | 2 | JB | 95-T/185-T | 1 | 2 | 1 | 2 |  | Step-1 |  |  |  |  | 127
[42 empty] | 810.66 |  |  |  | 78 | 810.66 | 810.66 | 500/204 |  |  |  | 16 | [15 empty] | TRACK
127 | 128 | BLS+0 |  |  |  |  | 281896 | 4718225.5 | 1122.881 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 44341.84 | 3 | AP46 | 45.727 |  | 509 | 308 | 0.61 |  |  |  |  | 3T-2T | 1 | 3 |  | 2 | 1 | 185-T/95-T | 2 | 1 | JB | 185-T/95-T | 2 | 1 | 1 | 2 |  | Step-1 |  |  |  |  | 128
[42 empty] | 188.48 |  |  |  | 79 | 290.8761 | 523.48 | 400/51 |  |  |  | 4
128 | 129 | BNS-3 |  |  |  |  | 281991.123 | 4718388.213 | 1100.75 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 44530.32 | 4.1 |  |  |  | 266 | 355 | 1.33 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 129
[42 empty] | 335 | [6 empty] | 400/51 |  |  |  | 7
129 | 130 | B30+12 |  |  |  |  | 282160.194 | 4718677.419 | 1015.336 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 44865.32 | 4.1 |  |  |  | 328 | 218 | 0.66 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 130
[42 empty] | 311.69 |  |  |  | 80 | 311.69 | 311.69 | 400/51 |  |  |  | 6
130 | 131 | BLS+6 |  |  |  |  | 282317.5 | 4718946.5 | 989.144 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 45177.01 | 5.1 | AP47 | -13.1374 |  | 394 | 1130 | 2.87 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 131
[42 empty] | 387.79 |  |  |  | 81 | 387.79 | 387.79 | 400/51 |  |  |  | 8 | [11 empty] | 27 W.S
131 | 132 | BLS+18 |  |  |  |  | 282432 | 4719317 | 701.737 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 45564.8 | 3 | AP48 | -35.6729 |  | 818 | -198 | -0.24 |  |  |  |  | 2T-3T | 2 | 3 |  | 1 | 3 | 95-T/185-T | 1 | 3 | JB | 95-T/185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 132
[42 empty] | 1155.1 |  |  |  | 82 | 1155.1 | 1155.1 | 500/204 |  |  |  | 22 | [15 empty] | TRACK, STREAM
132 | 133 | BLS+0 |  |  |  |  | 282065.49 | 4720412.41 | 829.133 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 46719.9 | 5.1 | AP49 | -55.6445 |  | 737 | 567 | 0.77 |  |  |  |  | 3T-2T | 2 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 133
[42 empty] | 294.97 |  |  |  | 83 | 294.97 | 294.97 | 400/51 |  |  |  | 6
133 | 134 | B30+9 |  |  |  |  | 281781.742 | 4720493.002 | 925.499 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 47014.87 | 3 |  |  |  | 305 | 306 | 1 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 134
[42 empty] | 278 |  |  |  | 84 | 278 | 278 | 400/51 |  |  |  | 5
134 | 135 | B30+0 |  |  |  |  | 281514.32 | 4720568.956 | 1037.418 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 47292.87 | 3 |  |  |  | 256 | 351 | 1.37 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 135
[42 empty] | 205.12 |  |  |  | 95 | 205.12 | 205.12 | 400/51 |  |  |  | 4
135 | 136 | BLS-6 |  |  |  |  | 281317 | 4720625 | 1109.691 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 47497.99 | 4.1 | AP50 | -23.7026 |  | 385 | 795 | 2.06 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 136
[42 empty] | 552.01 |  |  |  | 86 | 552.01 | 552.01 | 400/51 |  |  |  | 10
136 | 137 | B30-3 |  |  |  |  | 280770.163 | 4720549.638 | 1051.707 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 48050 | 4.1 |  |  |  | 436 | 409 | 0.94 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 137
[42 empty] | 315 |  |  |  | 87 | 317.5295 | 635 | 400/51 |  |  |  | 6
137 | 138 | BNS+9 |  |  |  |  | 280458.112 | 4720506.633 | 1010.947 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 48365 | 5.1 |  |  |  | 319 | 350 | 1.1 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 138
[42 empty] | 320 | [6 empty] | 400/51 |  |  |  | 6
138 | 139 | B30-3 |  |  |  |  | 280141.108 | 4720462.945 | 985.586 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 48685 | 3 |  |  |  | 395 | 542 | 1.37 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 139
[42 empty] | 457.39 |  |  |  | 88 | 457.39 | 457.39 | 400/51 |  |  |  | 9
139 | 140 | B30+0 |  |  |  |  | 279688 | 4720400.5 | 882.616 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 49142.39 | 5.1 | AP51 | 0.0458 |  | 431 | 239 | 0.55 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 140
[42 empty] | 392.39 |  |  |  | 89 | 392.39 | 392.39 | 400/51 |  |  |  | 8
140 | 141 | B30-3 |  |  |  |  | 279299.24 | 4720347.24 | 859.813 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 49534.78 | 3 | AP52 | 20.7861 |  | 371 | 599 | 1.61 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 141
[42 empty] | 336.84 |  |  |  | 90 | 336.84 | 336.84 | 400/51 |  |  |  | 7 | [15 empty] | TRACK
141 | 142 | BLS+0 |  |  |  |  | 278971.013 | 4720422.927 | 763.486 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 49871.62 | 3 |  |  |  | 656 | 653 | 1 |  |  |  |  | 2T-3T | 3 | 3 |  | 1 | 3 | 95-T/185-T | 1 | 3 | JB | 95-T/185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 142
[42 empty] | 948.26 |  |  |  | 91 | 948.26 | 948.26 | 500/204 |  |  |  | 19 | [11 empty] | 23 W.S |  |  |  | TRACK
142 | 143 | BLS+6 |  |  |  |  | 278047 | 4720636 | 598.056 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 50819.88 | 4.1 | AP53 | 5.9419 |  | 719 | -59 | -0.08 |  |  |  |  | 3T-2T | 3 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 143
[42 empty] | 425.34 |  |  |  | 92 | 425.34 | 425.34 | 400/51 |  |  |  | 8 | [15 empty] | TRACK
143 | 144 | BLC+18 |  |  |  |  | 277644.658 | 4720773.964 | 799.42 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 51245.22 | 4.1 |  |  |  | 473 | 530 | 1.12 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 144
[42 empty] | 434.45 |  |  |  | 93 | 434.45 | 434.45 | 400/51 |  |  |  | 8
144 | 145 | BLS-6 |  |  |  |  | 277233.701 | 4720914.883 | 1002.592 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 51679.67 | 5.1 |  |  |  | 496 | 1011 | 2.04 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 145
[42 empty] | 520.63 |  |  |  | 94 | 520.63 | 520.63 | 400/51 |  |  |  | 10
145 | 146 | B30-3 |  |  |  |  | 276741.22 | 4721083.756 | 968.426 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 52200.3 | 3 |  |  |  | 534 | 561 | 1.05 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 2 | 95-T | 2 | 2 |  | 95-T | 2 | 2 | 4 | 0 |  | Step-1 |  |  |  |  | 146
[42 empty] | 545.03 |  |  |  | 95 | 545.03 | 545.03 | 400/51 |  |  |  | 11
146 | 147 | B30+6 |  |  |  |  | 276225.658 | 4721260.544 | 917.316 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 52745.33 | 5.1 |  |  |  | 472 | 504 | 1.07 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 147
[42 empty] | 395.07 |  |  |  | 96 | 395.07 | 395.07 | 400/51 |  |  |  | 8
147 | 148 | BLS+0 |  |  |  |  | 275851.949 | 4721388.691 | 882.553 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 53140.4 | 3 |  |  |  | 704 | 1002 | 1.42 |  |  |  |  | 2T-3T | 3 | 3 |  | 1 | 3 | 95-T/185-T | 1 | 3 | JB | 95-T/185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 148
[42 empty] | 984.8 |  |  |  | 97 | 984.8 | 984.8 | 500/204 |  |  |  | 19 | [11 empty] | 28 W.S
148 | 149 | BLS+18 |  |  |  |  | 274920.395 | 4721708.124 | 640.999 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 54125.2 | 3 |  |  |  | 621 | 151 | 0.24 |  |  |  |  | 3T-2T | 3 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 149
[42 empty] | 232.54 |  |  |  | 98 | 232.54 | 232.54 | 400/51 |  |  |  | 5
149 | 150 | B30-3 |  |  |  |  | 274700.424 | 4721783.552 | 676.219 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 54357.74 | 4.1 | AP54 | 12.6789 |  | 286 | 636 | 2.22 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 150
[42 empty] | 327.74 |  |  |  | 99 | 327.74 | 327.74 | 400/51 |  |  |  | 6
150 | 151 | B30+12 |  |  |  |  | 274421.3 | 4721955.31 | 575.658 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 54685.48 | 4.1 | AP55 | -1.6816 |  | 341 | 201 | 0.59 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 151
[42 empty] | 339.86 |  |  |  | 100 | 339.86 | 339.86 | 400/51 |  |  |  | 7
151 | 152 | BLS+0 |  |  |  |  | 274126.75 | 4722124.85 | 545.768 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 55025.34 | 5.1 | AP56 | 2.237 |  | 697 | 173 | 0.25 |  |  |  |  | 2T-3T | 3 | 3 |  | 1 | 3 | 95-T/185-T | 1 | 3 | JB | 95-T/185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 152
[42 empty] | 1028.58 |  |  |  | 101 | 1028.58 | 1028.58 | 500/204 |  |  |  | 20 | [11 empty] | 25 W.S
152 | 153 | BLS-6 |  |  |  |  | 273256 | 4722672.37 | 766.262 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 56053.92 | 3 | AP57 | 11.4538 |  | 709 | 1026 | 1.45 |  |  |  |  | 3T-2T | 1 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 153
[42 empty] | 366.9 |  |  |  | 102 | 366.9 | 366.9 | 400/51 |  |  |  | 7
153 | 154 | BLC+0 |  |  |  |  | 272990.37 | 4722925.46 | 786.887 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 56420.82 | 5.1 |  | 1.9797 |  | 472 | 892 | 1.89 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 154
[42 empty] | 556.46 |  |  |  | 103 | 556.46 | 556.46 | 400/51 |  |  |  | 11 | [11 empty] | 10 W.S
154 | 155 | BLS+18 |  |  |  |  | 272601 | 4723323 | 622.952 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 56977.28 | 3 | AP58 | -3.3102 |  | 760 | -145 | -0.19 |  |  |  |  | 2T-3T | 3 | 3 |  | 2 | 3 | 95-T/185-T | 2 | 3 | JB | 95-T/185-T | 2 | 3 | 2 | 3 |  | Step-1 |  |  |  |  | 155
[42 empty] | 897.04 |  |  |  | 104 | 897.04 | 897.04 | 500/204 |  |  |  | 17 | [11 empty] | 19 W.S
155 | 156 | BLS+6 |  |  |  |  | 271937.36 | 4723926.54 | 928.583 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 57874.32 | 3 | AP59 | -0.0024 |  | 603 | 1154 | 1.91 |  |  |  |  | 3T-2T | 3 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 156
[42 empty] | 262.33 |  |  |  | 105 | 275.9423 | 550.12 | 400/51 |  |  |  | 5
156 | 157 | BNS+3 |  |  |  |  | 271743.275 | 4724103.033 | 939.33 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 58136.65 | 4.1 |  |  |  | 277 | 470 | 1.7 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 157
[42 empty] | 287.79 | [6 empty] | 400/51 |  |  |  | 6
157 | 158 | B30+6 |  |  |  |  | 271530.36 | 4724296.65 | 892.883 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 58424.44 | 4.1 | AP60 | -16.6385 |  | 369 | 605 | 1.64 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 158
[42 empty] | 423.92 |  |  |  | 106 | 423.92 | 423.92 | 400/51 |  |  |  | 8
158 | 159 | B30+12 |  |  |  |  | 271148.195 | 4724480.111 | 745.282 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 58848.36 | 5.1 |  |  |  | 440 | 565 | 1.28 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 159
[42 empty] | 390.43 |  |  |  | 107 | 390.43 | 390.43 | 400/51 |  |  |  | 8
159 | 160 | B30+9 |  |  |  |  | 270796.222 | 4724649.079 | 561.755 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 59238.79 | 3 |  |  |  | 471 | 413 | 0.88 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 160
[42 empty] | 476.11 |  |  |  | 108 | 476.11 | 476.11 | 400/51 |  |  |  | 9
160 | 161 | B30+3 |  |  |  |  | 270367 | 4724855.13 | 384.199 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 59714.9 | 5.1 | AP61 | 11.3608 |  | 416 | -39 | -0.09 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 161
[42 empty] | 321.46 |  |  |  | 109 | 321.46 | 321.46 | 400/51 |  |  |  | 6 | [11 empty] | 7 W.S |  |  |  | STREAM, TRACK
161 | 162 | BLC+18 |  |  |  |  | 270110.292 | 4725048.605 | 370.065 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 60036.36 | 3 |  |  |  | 455 | -40 | -0.09 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 162
[42 empty] | 528.17 |  |  |  | 110 | 528.17 | 528.17 | 400/51 |  |  |  | 10 | [11 empty] | 12 W.S |  |  |  | TRACK
162 | 163 | B30+12 |  |  |  |  | 269688.5 | 4725366.5 | 633.896 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 60564.53 | 3 | AP62 | 15.8227 |  | 431 | 755 | 1.75 |  |  |  |  | 2T-2T | 1 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 163
[42 empty] | 269.83 |  |  |  | 111 | 324.4525 | 629.83 | 400/51 |  |  |  | 5 | [15 empty] | 22O KV OHTL
163 | 164 | BNS+9 |  |  |  |  | 269525.464 | 4725581.503 | 685.571 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 60834.36 | 4.1 |  |  |  | 317 | 484 | 1.53 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 164
[42 empty] | 360 | [6 empty] | 400/51 |  |  |  | 7
164 | 165 | B30+3 |  |  |  |  | 269307.945 | 4725868.357 | 702.731 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 61194.36 | 4.1 |  |  |  | 344 | 209 | 0.61 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 165
[42 empty] | 325 |  |  |  | 112 | 349.1984 | 694.19 | 400/51 |  |  |  | 6
165 | 166 | BNS+3 |  |  |  |  | 269111.573 | 4726127.323 | 750.24 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 61519.36 | 5.1 |  |  |  | 350 | 390 | 1.11 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 166
[42 empty] | 369.19 | [6 empty] | 400/51 |  |  |  | 7
166 | 167 | B30-3 |  |  |  |  | 268888.5 | 4726421.5 | 798.687 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 61888.55 | 3 | AP63 | 7.5 |  | 447 | 458 | 1.02 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 167
[42 empty] | 520.81 |  |  |  | 113 | 520.81 | 520.81 | 400/51 |  |  |  | 10
167 | 168 | B30+12 |  |  |  |  | 268630.675 | 4726874.014 | 834.592 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 62409.36 | 5.1 |  |  |  | 441 | 261 | 0.59 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 168
[42 empty] | 345.49 |  |  |  | 114 | 345.49 | 345.49 | 400/51 |  |  |  | 7
168 | 169 | BLS-6 |  |  |  |  | 268459.64 | 4727174.2 | 947.947 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 62754.85 | 3 | AP64 | -15.488 |  | 293 | 772 | 2.63 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 169
[42 empty] | 224.51 |  |  |  | 115 | 224.51 | 224.51 | 400/51 |  |  |  | 4
169 | 170 | B30+9 |  |  |  |  | 268300.444 | 4727332.505 | 892.72 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 62979.36 | 3 |  |  |  | 282 | 468 | 1.66 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 170
[42 empty] | 320 |  |  |  | 116 | 320 | 320 | 400/51 |  |  |  | 6
170 | 171 | B30+9 |  |  |  |  | 268073.535 | 4727558.143 | 788.261 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 63299.36 | 4.1 |  |  |  | 345 | 360 | 1.04 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 171
[42 empty] | 335 |  |  |  | 117 | 335 | 335 | 400/51 |  |  |  | 7
171 | 172 | B30-3 |  |  |  |  | 267835.99 | 4727794.357 | 688.558 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 63634.36 | 4.1 |  |  |  | 331 | 154 | 0.47 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 172
[42 empty] | 305 |  |  |  | 118 | 310.1209 | 620 | 400/51 |  |  |  | 6
172 | 173 | BNS+3 |  |  |  |  | 267619.718 | 4728009.418 | 630.703 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 63939.36 | 5.1 |  |  |  | 316 | 391 | 1.24 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 173
[42 empty] | 315 | [6 empty] | 400/51 |  |  |  | 6 | [15 empty] | TRACK
173 | 174 | B30+6 |  |  |  |  | 267396.355 | 4728231.531 | 555.389 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 64254.36 | 3 |  |  |  | 333 | 235 | 0.71 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 174
[42 empty] | 340 |  |  |  | 119 | 319.1786 | 950 | 400/51 |  |  |  | 7
174 | 175 | BNS+9 |  |  |  |  | 267155.264 | 4728471.271 | 507.457 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 64594.36 | 5.1 |  |  |  | 336 | 370 | 1.1 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 175
[42 empty] | 325 | [6 empty] | 400/51 |  |  |  | 6
175 | 176 | BNS+0 |  |  |  |  | 266924.81 | 4728700.435 | 464.285 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 64919.36 | 3 |  |  |  | 310 | 362 | 1.17 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 176
[42 empty] | 285 | [6 empty] | 400/51 |  |  |  | 6
176 | 177 | B30+6 |  |  |  |  | 266722.72 | 4728901.393 | 400.211 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 65204.36 | 3 |  |  |  | 439 | 0 | 0 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 177
[42 empty] | 579.99 |  |  |  | 120 | 579.99 | 579.99 | 400/51 |  |  |  | 11 | [11 empty] | 13 W.S |  |  |  | TRACK, 11 KV OHTL, STREAM
177 | 178 | B30+0 |  |  |  |  | 266311.448 | 4729310.362 | 501.059 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 65784.35 | 4.1 |  |  |  | 475 | 351 | 0.74 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 178
[42 empty] | 342.57 |  |  |  | 121 | 342.57 | 342.57 | 400/51 |  |  |  | 7
178 | 179 | BLC+18 |  |  |  |  | 266068.541 | 4729551.909 | 599.511 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 66126.92 | 4.1 | AP65 | 1.4163 |  | 333 | 255 | 0.77 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 179
[42 empty] | 279.39 |  |  |  | 122 | 279.39 | 279.39 | 400/51 |  |  |  | 6
179 | 180 | B30+12 |  |  |  |  | 265875.357 | 4729753.749 | 724.4 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 66406.31 | 5.1 |  |  |  | 337 | 510 | 1.51 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 180
[42 empty] | 363.04 |  |  |  | 123 | 363.04 | 363.04 | 400/51 |  |  |  | 7
180 | 181 | B30+3 |  |  |  |  | 265624.33 | 4730016.025 | 810.236 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 66769.35 | 3 |  |  |  | 324 | 301 | 0.93 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 181
[42 empty] | 266.74 |  |  |  | 124 | 266.74 | 266.74 | 400/51 |  |  |  | 5
181 | 182 | B30+0 |  |  |  |  | 265439.9 | 4730208.72 | 885.462 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 67036.09 | 5.1 | AP66 | -18.0072 |  | 292 | 581 | 1.99 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 182
[42 empty] | 306.95 |  |  |  | 125 | 306.95 | 306.95 | 400/51 |  |  |  | 6
182 | 183 | B30-3 |  |  |  |  | 265169.5 | 4730354 | 883.559 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 67343.04 | 3 | AP67 | -5.7124 |  | 437 | 522 | 1.19 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 183
[42 empty] | 566.31 |  |  |  | 126 | 566.31 | 566.31 | 400/51 |  |  |  | 11
183 | 184 | B30+3 |  |  |  |  | 264646.432 | 4730571.044 | 835.023 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 67909.35 | 3 |  |  |  | 513 | 584 | 1.14 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 184
[42 empty] | 455.19 |  |  |  | 127 | 455.19 | 455.19 | 400/51 |  |  |  | 9
184 | 185 | BLS-6 |  |  |  |  | 264226 | 4730745.5 | 784.917 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 68364.54 | 4.1 | AP68 | -8.3543 |  | 731 | 1119 | 1.53 |  |  |  |  | 2T-3T | 3 | 3 |  | 1 | 3 | 95-T/185-T | 1 | 3 | JB | 95-T/185-T | 1 | 3 | 1 | 3 |  | Step-1 |  |  |  |  | 185
[42 empty] | 957.17 |  |  |  | 128 | 957.17 | 957.17 | 500/204 |  |  |  | 18 | [11 empty] | 32 W.S
185 | 186 | BLS-6 |  |  |  |  | 263298 | 4730980 | 485.74 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 69321.71 | 4.1 | AP69 | 38.0164 |  | 626 | 84 | 0.13 |  |  |  |  | 3T-2T | 1 | 3 |  | 3 | 1 | 185-T/95-T | 3 | 1 | JB | 185-T/95-T | 3 | 1 | 1 | 3 |  | Step-1 |  |  |  |  | 186
[42 empty] | 250.03 |  |  |  | 129 | 288.2616 | 1069.45 | 400/51 |  |  |  | 5 | [15 empty] | TRACK
186 | 187 | BNS+3 |  |  |  |  | 263144.753 | 4731177.549 | 476.623 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 69571.74 | 5.1 |  |  |  | 303 | 341 | 1.13 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 187
[42 empty] | 355 | [6 empty] | 400/51 |  |  |  | 7
187 | 188 | BNS-3 |  |  |  |  | 262927.161 | 4731458.046 | 470.73 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 69926.74 | 3 |  |  |  | 320 | 428 | 1.34 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 188
[42 empty] | 282 | [6 empty] | 400/51 |  |  |  | 5
188 | 189 | BNS+0 |  |  |  |  | 262754.313 | 4731680.863 | 429.901 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 70208.74 | 5.1 |  |  |  | 236 | 355 | 1.5 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 189
[42 empty] | 182.42 | [6 empty] | 400/51 |  |  |  | 4
189 | 190 | B30-3 |  |  |  |  | 262642.5 | 4731825 | 388.521 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 70391.16 | 3 | AP70 | -20.0502 |  | 393 | 137 | 0.35 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 190
[42 empty] | 597.62 |  |  |  | 130 | 597.62 | 597.62 | 400/51 |  |  |  | 11 | [11 empty] | 15 W.S |  |  |  | TRACK, 11 KV OHTL, STREAM
190 | 191 | B60+12 |  |  |  |  | 262136.5 | 4732143 | 372.371 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 70988.78 | 3 | AP71 | -52.5504 |  | 423 | 432 | 1.02 |  |  |  |  | 2T-2T | 2 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 191
[42 empty] | 248.93 |  |  |  | 131 | 248.93 | 248.93 | 400/51 |  |  |  | 6 | [15 empty] | TRACK
191 | 192 | BLC+0 |  |  |  |  | 261903.19 | 4732056.22 | 382.422 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 71237.71 | 4.1 |  | -1.8716 |  | 388 | 430 | 1.11 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 192
[42 empty] | 525.96 |  |  |  | 132 | 525.96 | 525.96 | 400/51 |  |  |  | 9
192 | 193 | B30+3 |  |  |  |  | 261416.48 | 4731856.86 | 360.123 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 71763.67 | 4.1 | AP72 | -1.9974 |  | 535 | 512 | 0.96 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 2 | 95-T | 1 | 2 |  | 95-T | 1 | 2 | 3 | 0 |  | Step-1 |  |  |  |  | 193
[42 empty] | 544.08 |  |  |  | 133 | 544.08 | 544.08 | 400/51 |  |  |  | 11 | [15 empty] | TRACK
193 | 194 | B30+3 |  |  |  |  | 260920.49 | 4731633.205 | 351.459 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 72307.75 | 5.1 |  |  |  | 451 | 209 | 0.46 |  |  |  |  | 2T-2T | 3 | 3 |  | 2 | 1 | 95-T | 2 | 1 |  | 95-T | 2 | 1 | 3 | 0 |  | Step-1 |  |  |  |  | 194
[42 empty] | 349.97 |  |  |  | 134 | 349.97 | 349.97 | 400/51 |  |  |  | 7
194 | 195 | BLC-6 |  |  |  |  | 260601.461 | 4731489.348 | 434.26 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 72657.72 | 3 |  |  |  | 344 | 659 | 1.92 |  |  |  |  | 2T-2T | 3 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 195
[42 empty] | 330.02 |  |  |  | 135 | 369.6389 | 729.44 | 400/51 |  |  |  | 7
195 | 196 | BNS+0 |  |  |  |  | 260300.612 | 4731353.687 | 402.913 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 72987.74 | 3 |  |  |  | 368 | 479 | 1.3 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 196
[42 empty] | 399.42 | [6 empty] | 400/51 |  |  |  | 8 | [15 empty] | TRACK
196 | 197 | B60+0 |  |  |  |  | 259936.5 | 4731189.5 | 336.162 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 73387.16 | 3 | AP73 | -32.7969 |  | 405 | 39 | 0.1 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 | JB | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 197
[42 empty] | 400.6 |  |  |  | 136 | 346.9527 | 596.91 | 400/51 |  |  |  | 8 | [15 empty] | TRACK, 11 KV OHTL
197 | 198 | BNS+6 |  |  |  |  | 259718.718 | 4730853.263 | 388.674 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 73787.76 | 3 |  |  |  | 301 | 355 | 1.18 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 198
[42 empty] | 196.31 | [6 empty] | 400/51 |  |  |  | 4
198 | 199 | B30-3 |  |  |  |  | 259612 | 4730688.5 | 418.416 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 73984.07 | 3 | AP74 | 29.2608 |  | 275 | 365 | 1.33 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 199
[42 empty] | 352.67 |  |  |  | 137 | 289.0773 | 783.47 | 400/51 |  |  |  | 7
199 | 200 | BNS-3 |  |  |  |  | 259300.058 | 4730523.976 | 427.978 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 74336.74 | 3 |  |  |  | 266 | 341 | 1.28 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 200
[42 empty] | 180 | [6 empty] | 400/51 |  |  |  | 4
200 | 201 | BNS+0 |  |  |  |  | 259140.845 | 4730440.005 | 417.995 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 74516.74 | 3 |  |  |  | 217 | 351 | 1.62 |  |  |  |  | SS |  |  |  | 1 | 1 | 95-S | 1 | 1 |  | 95-S | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 201
[42 empty] | 250.8 | [6 empty] | 400/51 |  |  |  | 5
201 | 202 | B30-3 |  |  |  |  | 258919 | 4730323 | 381.032 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 74767.54 | 3 | AP75 | 27.4537 |  | 319 | 225 | 0.71 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 202
[42 empty] | 383.37 |  |  |  | 138 | 383.37 | 383.37 | 400/51 |  |  |  | 7 | [15 empty] | ROAD, TRACK
202 | 203 | B30+3 |  |  |  |  | 258535.64 | 4730320.63 | 349.971 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 75150.91 | 3 | AP76 | 26.9234 |  | 408 | 423 | 1.04 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 203
[42 empty] | 430.58 |  |  |  | 139 | 430.58 | 430.58 | 400/51 |  |  |  | 8 | [15 empty] | TRACK, 35 KV OHTL
203 | 204 | B60+9 |  |  |  |  | 258150.53 | 4730513.22 | 312.108 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 75581.49 | 3 | AP77 | 43.3553 |  | 421 | 346 | 0.82 |  |  |  |  | 2T-2T | 1 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 204
[42 empty] | 410.69 |  |  |  | 140 | 410.69 | 410.69 | 400/51 |  |  |  | 8 | [15 empty] | TRACK
204 | 205 | B90+0 |  |  |  |  | 258009.56 | 4730898.95 | 316.003 | [5 empty] | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet |  | Not Yet | 75992.18 | 3 | AP78 | -37.8984 |  | 247 | 270 | 1.09 |  |  |  |  | 2T-2T | 2 | 3 |  | 1 | 1 | 95-T | 1 | 1 |  | 95-T | 1 | 1 | 2 | 0 |  | Step-1 |  |  |  |  | 205
[42 empty] | 82.05 |  |  |  | 141 | 82.05 | 82.05 | 400/51 |  |  |  | 3
205 | G2 | GANTRY |  |  |  |  | 257939.997 | 4730942.462 | 316.819 | [28 empty] | 76074.23 |  | AP79/SS |  |  | 41 | 39 | 0.95 |  |  |  |  | 2T |  |  |  | 1 |  | 95-TSJ | 1 |  | JB | 95-TSJ | 1 |  | 1 | 0 | [6 empty] | G2
Formulas:
JB : = IF([JB :]="","Not Yet",IF([JB :]=TODAY(),"Today Completed",IF([JB :]=TODAY()+1,"Tomorrow's Plan",IF([JB :]<TODAY(),"Completed","Not Yet"))))
4
3
2
1

## Summary
Contractor: | [7 empty] | Customer: | Consultant:
STRUCTURE LIST
LOT 1: CONSTRUCTION OF 500KV JVARI - TSKALTUBO OVERHEAD LINE
SUMMARY LIST
FOUNDATIONS
| Towers | Total | Good Soil | Poor Soil | Soft Rock | Hard Rock | Water Logged | LINE'S TOTAL LENGTH (m): | 76074.23
|  |  | FDN1 | FDN2 | FDN3 | FDN4 | FDN5 | TOTAL LINE LENGTH WITH ACO 400/51 CONDUCTOR (m): | 69010.953
| BNS-6 | 0 | 0 |  |  |  |  | TOTAL LINE LENGTH WITH ACYC 500/204 CONDUCTOR (m): | 8530.515
| BNS-3 | 8 | 8
| BNS+0 | 4 | 4 |  |  |  |  | PHASE CONDUCTOR
| BNS+3 | 16 | 16 |  |  |  |  | Insulator Strings Sets
| BNS+6 | 12 | 12
| BNS+9 | 8 | 8 |  |  |  |  | Type | Code | Set/ Phase | SC | Total Sets
| BNS+12 | 6 | 6
[8 empty] | SINGLE SUSPENSION SET (ACO 400/51) | SS | 43 | 3 | 129
[8 empty] | DOUBLE SUSPENSION SET (ACO 400/51) | DS | 11 | 3 | 33
| BLC-6 | 2 | 2 |  |  |  |  | DOUBLE TENSION (ACO 400/51) | 2T | 270 | 3 | 810
| BLC+0 | 3 | 3 |  |  |  |  | TRIPLE TENSION SET (ACYC 500/204) | 3T | 22 | 3 | 66
| BLC+6 | 0 | 0 |  |  |  |  | JUMPER SUSPENSION SET (ACO 400/51) | JS | 358 | 1 | 358
| BLC+12 | 1 | 1 |  |  |  |  | Type | Code | Set/ Phase | SC | Total Sets / Units
| BLC+18 | 4 | 4
| BLS-6 | 8 | 8 |  |  |  |  | 210 kN SILICONE SUSPENSION INSULATORS |  | 195
| BLS+0 | 7 | 7 |  |  |  |  | 210 kN SILICONE INSULATORS FOR DOUBLE TENSION SET |  | 1620
| BLS+6 | 4 | 4 |  |  |  |  | 320 kN SILICONE INSULATORS FOR TRIPLE TENSION SET |  | 198
| BLS+12 | 2 | 2 |  |  |  |  | 210 kN JUMPER SUSPENSION INSULATORS |  | 358
| BLS+18 | 3 | 3 |  |  |  |  | RIGID SPACER |  | 780
| B30-6 | 0 | 0 |  |  |  |  | SPACER DAMPER FOR ACO 400/51 |  | 1045 | 3 | 3135
| B30-3 | 39 | 39 |  |  |  |  | SPACER DAMPER FOR ACYC 500/204 |  | 131 | 3 | 393
| B30+0 | 12 | 12 |  |  |  |  | STOCKBRIDGE DAMPER FOR ACO 400/51 | UT3 | 420 | 3 | 3780
| B30+3 | 13 | 13 |  |  |  |  | STOCKBRIDGE DAMPER FOR ACYC 500/204 | UT3 | 40 | 3 | 360
| B30+6 | 7 | 7 |  |  |  |  | COUNTER WEIGHT (50kg) |  | 10 | 3 | 30
| B30+9 | 4 | 4
| B30+12 | 13 | 13 |  |  |  |  | OPGW
| B60-6 | 0 | 0 |  |  |  |  | Type |  |  | Code | Total
| B60-3 | 6 | 6 |  |  |  |  | SUSPENSION SET (95 TYPE - 24 FIBERS) |  |  | 95-S | 54
| B60S-3 | 0 | 0 |  |  |  |  | TENSION NON-JOINT SET (95 TYPE - 24 FIBERS) |  |  | 95-T | 115
| B60+0 | 1 | 1 |  |  |  |  | TENSION JOINT SET DOUBLE (95 TYPE - 24 FIBERS) |  |  | 95-T | 18
| B60+3 | 2 | 2 |  |  |  |  | TENSION JOINT SET SINGLE (95 TYPE - 24 FIBERS) |  |  | 95-TSJ | 2
| B60+6 | 2 | 2 |  |  |  |  | TENSION JOINT SET DOUBLE (185 TYPE - 24 FIBERS) |  |  | 185-T | 7
| B60+9 | 1 | 1 |  |  |  |  | STOCKBRIDGE DAMPER FOR (95 TYPE - 24 FIBERS) |  |  | UT2 | 416
| B60+12 | 3 | 3 |  |  |  |  | STOCKBRIDGE DAMPER FOR (185 TYPE - 24 FIBERS) |  |  | UT2 | 40
| B90-3 | 2 | 2 |  |  |  |  | JOINT BOX |  |  | JB | 31
| B90+0 | 1 | 1
| B90S+0 | 0 | 0 |  |  |  |  | EARTHWIRE
| B90+3 | 0 | 0 |  |  |  |  | Type |  |  | Code | Total
| B90+6 | 0 | 0 |  |  |  |  | SUSPENSION SET (ACS-95) |  |  | 95-S | 54
| B90+9 | 1 | 1 |  |  |  |  | ANCHOR UNIT (ACS-95) |  |  | 95-T | 115
| B90+12 | 1 | 1 |  |  |  |  | ANCHOR UNIT (ACS-185) |  |  | 185-T | 7
| B90C | 2 | 2 |  |  |  |  | STOCKBRIDGE DAMPER FOR (ACS-95)) |  |  | UT1 | 402
| Total | 198 | 198 | 0 | 0 | 0 | 0 | STOCKBRIDGE DAMPER FOR (ACS-185)) |  |  | UT2 | 58

## Spans
No. | Wind Span | Weight Span
G1 | 43 | 53
1 | 183 | 224
2 | 280 | 250
3 | 291 | 353
4 | 302 | 234
5 | 321 | 361
6 | 274 | 249
7 | 308 | 343
8 | 398 | 378
9 | 375 | 414
10 | 358 | 317
11 | 345 | 350
12 | 338 | 374
13 | 345 | 286
14 | 345 | 383
15 | 342 | 376
16 | 365 | 296
17 | 386 | 439
18 | 352 | 396
19 | 325 | 262
20 | 348 | 385
21 | 388 | 331
22 | 420 | 474
23 | 428 | 362
24 | 420 | 476
25 | 386 | 456
26 | 360 | 247
27 | 349 | 376
28 | 333 | 382
29 | 356 | 450
30 | 376 | 223
31 | 340 | 382
32 | 315 | 346
33 | 378 | 274
34 | 437 | 493
35 | 458 | 601
36 | 460 | 299
37 | 433 | 495
38 | 363 | 418
39 | 333 | 375
40 | 323 | 216
41 | 350 | 406
42 | 386 | 489
43 | 339 | 159
44 | 353 | 457
45 | 329 | 167
46 | 272 | 339
47 | 305 | 569
48 | 263 | 69
49 | 236 | 43
50 | 300 | 461
51 | 392 | 297
52 | 385 | 443
53 | 278 | 529
54 | 340 | 57
55 | 343 | 367
56 | 272 | 535
57 | 353 | 597
58 | 401 | 37
59 | 354 | 253
60 | 303 | 182
61 | 304 | 356
62 | 321 | 223
63 | 386 | 844
65 | 410 | 101
66 | 425 | 629
67 | 504 | 358
68 | 432 | 418
69 | 314 | 94
70 | 277 | 516
71 | 323 | 456
72 | 370 | 273
73 | 375 | 411
74 | 379 | 430
75 | 412 | 397
77 | 412 | 536
78 | 314 | 159
79 | 376 | 303
80 | 487 | 101
81 | 386 | 860
82 | 318 | 410
83 | 326 | 353
84 | 338 | 410
85 | 317 | 260
86 | 279 | 260
87 | 264 | 361
88 | 283 | 442
89 | 378 | 155
90 | 421 | 272
91 | 361 | 417
92 | 314 | 214
93 | 323 | 444
94 | 336 | 236
95 | 361 | 311
96 | 305 | 567
97 | 336 | 135
98 | 438 | 537
99 | 433 | 180
100 | 378 | 273
101 | 302 | 343
102 | 288 | 550
103 | 396 | 623
104 | 432 | 246
105 | 480 | 322
106 | 402 | 672
107 | 322 | 552
108 | 429 | 80
109 | 348 | 277
110 | 262 | 394
111 | 232 | -44
112 | 258 | 310
113 | 303 | 359
114 | 313 | 361
115 | 309 | 227
116 | 283 | 365
117 | 258 | 311
118 | 344 | 187
119 | 549 | 325
120 | 437 | 561
121 | 413 | 1024
122 | 470 | 22
123 | 276 | 341
124 | 337 | 166
125 | 356 | 266
126 | 372 | 220
127 | 655 | 1506
128 | 509 | 308
129 | 266 | 355
130 | 328 | 218
131 | 394 | 1130
132 | 818 | -198
133 | 737 | 567
134 | 305 | 306
135 | 256 | 351
136 | 385 | 795
137 | 436 | 409
138 | 319 | 350
139 | 395 | 542
140 | 431 | 239
141 | 371 | 599
142 | 656 | 653
143 | 719 | -59
144 | 473 | 530
145 | 496 | 1011
146 | 534 | 561
147 | 472 | 504
148 | 704 | 1002
149 | 621 | 151
150 | 286 | 636
151 | 341 | 201
152 | 697 | 173
153 | 709 | 1026
154 | 472 | 892
155 | 760 | -145
156 | 603 | 1154
157 | 277 | 470
158 | 369 | 605
159 | 440 | 565
160 | 471 | 413
161 | 416 | -39
162 | 455 | -40
163 | 431 | 755
164 | 317 | 484
165 | 344 | 209
166 | 350 | 390
167 | 447 | 458
168 | 441 | 261
169 | 293 | 772
170 | 282 | 468
171 | 345 | 360
172 | 331 | 154
173 | 316 | 391
174 | 333 | 235
175 | 336 | 370
176 | 310 | 362
177 | 439 | 0
178 | 475 | 351
179 | 333 | 255
180 | 337 | 510
181 | 324 | 301
182 | 292 | 581
183 | 437 | 522
184 | 513 | 584
185 | 731 | 1119
186 | 626 | 84
187 | 303 | 341
188 | 320 | 428
189 | 236 | 355
190 | 393 | 137
191 | 423 | 432
192 | 388 | 430
193 | 535 | 512
194 | 451 | 209
195 | 344 | 659
196 | 368 | 479
197 | 405 | 39
198 | 301 | 355
199 | 275 | 365
200 | 266 | 341
201 | 217 | 351
202 | 319 | 225
203 | 408 | 423
204 | 421 | 346
205 | 247 | 270
G2 | 41 | 39